## Config
PROJECT CONFIGURATION — VARIABLE DEFINITIONS
All sheets reference these cells. Change a value here and it propagates everywhere automatically.
SECTION 1 - PROJECT IDENTITY
Variable Name | Value | Unit / Notes | Used In | Updated | Source
ProjectName | Galvanizing System | Project Title | All Sheets | 2026 | Client Brief
ProjectNumber | PRJ-26001 | Project ID | All Sheets – Headers | 2026 | PM System
ClientName | Howest - Cyber3Lab | Client | Cover | 2026 | Contract
SiteLocation | Building J - Cyber3Lab, Howest Brugge, Belgium | Location | Cover, TBL | 2026 | Site Survey
SECTION 2 - PLC PLATFORM (WAGO CC100 751-9402)
Variable Name | Value | Unit / Notes | Used In | Updated | Source
PLCPlatform | WAGO Compact Controller 100 | Brand / Series | Cover, IO List, TBL | 2026 | WAGO 751-9402 Datasheet
PLCModelNo | 751-9402 | Part Number | Cover, IO List, TBL | 2026 | wago.com/global/p/751-9402
PLCProgEnv | CODESYS V3.5 | IDE / Runtime | Cover, Wiring Legend | 2026 | WAGO firmware docs
PLCComms | Modbus TCP, EtherNet/IP, PROFINET, EtherCAT, BACnet, MQTT | Protocols | Cover, Legend | 2026 | WAGO product page
PLCConnType | picoMAX® CAGE CLAMP® push-in | I/O Connector Type | IO List, TBL | 2026 | WAGO datasheet
PLCRating | IP20 / DIN Rail Mount / 24 VDC | Protection / Mounting | Cover, TBL | 2026 | WAGO 751-9402 spec
SECTION 3 - ELECTRICAL SPECIFICATIONS
Variable Name | Value | Unit / Notes | Used In | Updated | Source
VoltageControl | 24 VDC | Control Supply | Cover, IO List, TBL, Legend | 2026 | IEC 60204-1
VoltagePower | 230 V AC, 50 Hz | Main Supply | Cover, TBL | 2026 | Site supply spec
EnclosureRating | IP65 (Field) / IP54 (Panel) | IP Rating | Cover, TBL | 2026 | IEC 60529
SECTION 4 - WAGO CC100 I/O CHANNEL MAP (On-Board I/O)
Variable Name | Value | Unit / Notes | Used In | Updated | Source
I/O Tag | Channel Label | CODESYS Addr | Signal Type | Connector | Notes
DI10001 | DI.1 | %IX0.0 | DI 24VDC | X11 – Pin 1 | On-board: 8 dedicated DI, 2.8 mA
DI10002 | DI.2 | %IX0.1 | DI 24VDC | X11 – Pin 2 | 24 VDC sinking, RC filter 5µs
DI10003 | DI.3 | %IX0.2 | DI 24VDC | X11 – Pin 3
DI10004 | DI.4 | %IX0.3 | DI 24VDC | X11 – Pin 4
DI10005 | DI.5 | %IX0.4 | DI 24VDC | X11 – Pin 5
DI10006 | DI.6 | %IX0.5 | DI 24VDC | X11 – Pin 6
DI10007 | DI.7 | %IX0.6 | DI 24VDC | X11 – Pin 7
DI10008 | DI.8 | %IX0.7 | DI 24VDC | X11 – Pin 8
DI10009 | DIO.1 | %IX1.0 | DI/DO 24VDC | X12 – Pin 1 | 8 configurable DIO; set in CODESYS
DI10010 | DIO.2 | %IX1.1 | DI/DO 24VDC | X12 – Pin 2 | Configure as DI or DO per channel
DI10011 | DIO.3 | %IX1.2 | DI/DO 24VDC | X12 – Pin 3
DI10012 | DIO.4 | %IX1.3 | DI/DO 24VDC | X12 – Pin 4
DO20001 | DIO.5 | %QX1.4 | DO 24VDC | X12 – Pin 5 | Configured as DO, 0.5 A max
DO20002 | DIO.6 | %QX1.5 | DO 24VDC | X12 – Pin 6
DO20003 | DIO.7 | %QX1.6 | DO 24VDC | X12 – Pin 7
DO20004 | DIO.8 | %QX1.7 | DO 24VDC | X12 – Pin 8
DO20005 | DIO.1* | %QX1.0 | DO 24VDC | X12 – Pin 1 | If needed; DIO re-assigned
DO20006 | DIO.2* | %QX1.1 | DO 24VDC | X12 – Pin 2
DO20007 | DIO.3* | %QX1.2 | DO 24VDC | X12 – Pin 3
AI30001 | AI.1 | %IW0 | AI 4-20mA / 0-10V | X13 – AI1+/AI1- | 2 dedicated AI; 16-bit resolution
AI30002 | AI.2 | %IW2 | AI 4-20mA / 0-10V | X13 – AI2+/AI2-
AI30003 | NI.1 | %IW4 | NI1K/PT1K RTD | X14 – NI1+/NI1- | 2 RTD inputs (NI1000/PT1000)
AO40001 | AIO.1 | %QW0 | AO 4-20mA / 0-10V | X13 – AIO1 | 2 configurable AI/AO; 12-bit
SECTION 5 - STANDARDS & REFERENCES
Variable Name | Value | Unit / Notes | Used In | Updated | Source
Std_Wiring | IEC 60204-1 | Safety of Machinery | Cover, Legend | 2026 | IEC
Std_WireColor | IEC 60446 | Wire Colour Identification | Legend | 2026 | IEC
Std_Cables | AS/NZS 5000.1 | Electric Cables – Polymeric | Legend | 2026 | Standards AU
Std_LocalWire | AS/NZS 3000 | Wiring Rules (Australia/NZ) | Cover, Legend | 2026 | Standards AU
Std_PLC_HW | IEC 61131-2 | PLCs – Equipment Requirements | IO List, Legend | 2026 | IEC
SECTION 6 - DOCUMENT REFERENCES
Variable Name | Value | Unit / Notes | Used In | Updated | Source
DrawingRef | EL-PLC-001 to EL-PLC-048 | Drawing Range | Cover | 2026 | Doc Control
PreparedBy | Howest - Cyber3Lab | Prepared By | Cover | 2026
ApprovedBy | Laurens Singier | Approved By | Cover | 2026
RevStatus | REV A - Issued for Construction | Revision Status | Cover | 2026
Engineer | Attila Peter Szucs | Lead Engineer | Cover | 2026
Discipline | Electrical / Instrumentation | Discipline | Cover | 2026

## Cover
INDUSTRIAL PLC CABLING & WIRING SYSTEM
Project Documentation Package
PROJECT INFORMATION
Project Name: | Galvanizing System | Project No.: | PRJ-26001
Client: | Howest - Cyber3Lab | Site Location: | Building J - Cyber3Lab, Howest Brugge, Belgium
Engineer: | Attila Peter Szucs | Discipline: | Electrical / Instrumentation
Drawing Ref: | EL-PLC-001 to EL-PLC-048 | PLC Platform: | WAGO Compact Controller 100 (751-9402)
Voltage (Control): | 24 VDC | Voltage (Power): | 230 V AC, 50 Hz
Enclosure Rating: | IP65 (Field) / IP54 (Panel) | Standard: | IEC 60204-1 / AS/NZS 3000
Prepared By: | Howest - Cyber3Lab | Date:
Approved By: | Laurens Singier | Rev Status: | REV A - Issued for Construction
DOCUMENT INDEX
Sheet / Tab | Document Title | Description | Status
Cover | Project Cover Sheet | Project information and document index
Cable Schedule | Cable Schedule | Full cable listing with specs, routing & terminations
IO List | PLC I/O List | Digital and analog I/O assignments with signal details
Terminal Block Layout | Terminal Block Layout | Panel terminal block assignments and wire mapping
Cable Drum Register | Cable Drum Register | Drum tracking, lengths issued and remaining
Wiring Legend | Wiring Legend & Standards | Color codes, abbreviations, cable types, standards ref
GENERAL NOTES
1. All cabling shall be installed in accordance with IEC 60204-1 and local wiring regulations.
2. Signal cables (4–20 mA) must be segregated from power cables (minimum 200 mm separation).
3. All cable screens/shields to be grounded at ONE end only (control panel end) unless otherwise noted.
4. Minimum cable bending radius: 6× cable OD (multi-core), 8× cable OD (armoured).
5. All field terminations to use ferrules (bootlace type). Crimping tool: Weidmuller or equivalent.
6. WAGO CC100 I/O: 8 DI (X12), 8 configurable DIO (X5), 2 AI + 2 AIO (X6), 2 NI/PT (X13). All on-board; 24 VDC.
7. Motor cables must be shielded (VFD duty) where inverter drives are installed.

## Cable Schedule
CABLE SCHEDULE — PRJ-26001
Project: PRJ-26001 ¦ Project No: PRJ-26001 ¦ PLC: WAGO Compact Controller 100 (751-9402) ¦ Rev: REV A - Issued for Construction
# | Cable No. | From (Source) | From Location | From Terminal | To (Destination) | To Location | To Terminal | Cable Type | Cores | Size mm² | Volt Rating | Shield | Length m | Conduit / Tray | Status | Rev
1 | NET-W101 | WAGO 852-1812 | Panel Cabinet | X3 | WAGO CC100 751-9402 | Panel Cabinet | X1 | SF/UTP Cat6a | 4P | 24 AWG | 100V | No | 50 cm |  | Installed | C
2 | NET-W102 | WAGO 852-1812 | Panel Cabinet | X1 | EXT_NETWORK_UPLINK | External | - | SF/UTP Cat6a | 4P | 24 AWG | 100V | No | 3 m |  | Installed | C
3 | NET-W103 | WAGO 852-1812 | Panel Cabinet | X8 | EXT_SERVICE_CON | External | - | SF/UTP Cat6a | 4P | 24 AWG | 100V | No | 2 m |  | Installed | C
4 | NET-W104 | WAGO 852-1812 | Panel Cabinet | X2 | WAGO Web Panel 400 (A1) | Panel Cabinet | X1:ETH | SF/UTP Cat6a | 4P | 24 AWG | 100V | No | 2 m |  | Installed | C
5 | PWR-W10 | Power Outlet (230V AC) | Panel Cabinet | X1 (L/N/PE) | G1 - QUINT POWER AC/DC Converter | Panel Cabinet | X10 | ÖLFLEX CLASSIC 100 | 3G | 1.5 mm² | 300/500V | No | 3 m |  | Installed | C
6 | PWR-W11 | Power Outlet (230V AC) | Panel Cabinet | X2 (L/N/PE) | G2 - WAGO 787-1202 AC/DC Converter | Panel Cabinet | X10 | ÖLFLEX CLASSIC 100 | 3G | 1.5 mm² | 100/240V | No | 1.9 m |  | Installed | C
7 | PWR-W13 | 24V DC Distribution Block (X24V) | Panel Cabinet | 24V_PLC_1 / 0V_PLC_1 | WAGO CC100 751-9402 (KF10) | Panel Cabinet | 86.1 / 86.2 | 2xAWG20 | 2 | 0.5 mm² | 24V DC | No | 50 cm |  | Installed | C
8 | PWR-W14 | 24V DC Distribution Block (X24V) | Panel Cabinet | 24V_SW1 / 0V_SW1 | WAGO 852-1812 Switch (KF1) | Panel Cabinet | PWR+ / PWR- | 2xAWG20 | 2 | 0.5 mm² | 24V DC | No | 30 cm |  | Installed | C
9 | PWR-W15 | 24V DC Distribution Block (X0V) | Panel Cabinet | +-24V_PLC_X5:1 / +-0V_PLC_X5:2 | WAGO CC100 751-9402 (KF10) | Panel Cabinet | X5 (DIO power) | 2xAWG20 | 2 | 0.5 mm² | 24V DC | No | 25 cm |  | Installed | C
10 | HMI-W12 | 24V DC Distribution Block (X24V) | Panel Cabinet | +-24V_HMI_1 / +-0V_HMI_1 / +-PE_HMI_1 | WAGO Web Panel 400 (A1) | Panel Cabinet | X3.1 / X3.2 / X3.3 | 3xAWG20 | 3 | 0.5 mm² | 24V DC | No | 30 cm |  | Installed | C
11 | PLC-W10 | 0V DC Distribution Block (X0V) | Panel Cabinet | +-0V_PLC_X12:2 | WAGO CC100 751-9402 (KF10) | Panel Cabinet | X12.2 (0V ref) | 1xAWG20 | 1 | 0.5 mm² | 24V DC | No | 50 cm |  | Installed | C
12 | PLC-W11 | 24V DC Distribution Block (X24V) | Panel Cabinet | +-24V_PLC_X12:3 | S1 - E-Stop / Control Button | Panel Cabinet | COM | 1xAWG20 | 1 | 0.5 mm² | 24V DC | No | 50 cm |  | Installed | C
13 | PLC-W12 | WAGO CC100 751-9402 (KF10) | Panel Cabinet | X12.3 (DI input) | S1 - E-Stop / Control Button | Panel Cabinet | NO | 1xAWG20 | 1 | 0.5 mm² | 24V DC | No | 50 cm |  | Installed | C
14 | PLC-W101 | WAGO CC100 751-9402 (KF10) | Panel Cabinet | X1 (ETH) | WAGO 852-1812 Switch (KF1) | Panel Cabinet | LNK X3 | SF/UTP Cat6a | 4P | 24 AWG | 100V | No | 50 cm |  | Installed | C
15 | PLC-W102 | WAGO CC100 751-9402 (KF10) | Panel Cabinet | X5:DIO1 / DIO2 / DIO3 | P1 (Red) / P2 (Blue) / P3 (Green) Indicators | Panel Cabinet | Pin 1 (each) | 3xAWG20 | 3 | 0.5 mm² | 24V DC | No | 60 cm |  | Installed | C
16 | PLC-W103 | P1 (Red) / P2 (Blue) / P3 (Green) Indicators | Panel Cabinet | Pin 2 (return, each) | 0V DC Distribution Block (X0V) | Panel Cabinet | +-0V_P1/P2/P3_X1 | 3xAWG20 | 3 | 0.5 mm² | 24V DC | No | 60 cm |  | Installed | C
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
50

## IO List
SYSTEM I/O & POWER DISTRIBUTION LIST — PRJ-26001 ¦ WAGO Compact Controller 100 (751-9402)
# | I/O Tag | Description | Cable / Wire No. | Connector | CODESYS Addr | Channel Label | Signal Type | Range / State | Wire + | Wire - | Screen | Terminal | Remarks
DIGITAL INPUTS (DI) - 24 VDC ¦ CC100: X12 (DI.1–DI.8)
1 | X12:2 | PLC 0V | 20 AWG |  |  |  | DC | 0 VDC |  | -X0V
2 | X12:3 | Button 24V | 20 AWG |  | %IX6.0 |  | DI | 24 VDC | Button 24V
3
4
5
DIGITAL OUTPUTS (DO) - 24 VDC ¦ CC100: X5 (DIO channels configured as DO)
1 | X5:3 | Shneider Electric - Harmony XB5AVB4 (Red) | 20 AWG |  | %QX0.0 |  |  | 24VDC
2 | X5:4 | Shneider Electric - Harmony XB5AVB6 (Blue) | 20 AWG |  | %QX0.1 |  |  | 24VDC
3 | X5:5 | Shneider Electric - Harmony XB5AVB3 (Green) | 20AWG |  | %QX0.2 |  |  | 24VDC
4
5
ANALOG INPUTS (AI) - 4-20 mA / 0-10 V / NI1K / PT1K ¦ CC100: X13 (AI, AIO) and X14 (NI/PT)
1
2
3
4
5
ANALOG OUTPUTS (AO) - 4-20 mA / 0-10 V ¦ CC100: X13 (AIO channels configured as AO)
1
2
3
4
5
24V DC BUS - POWER DISTRIBUTION ¦ 5 Inputs / 5 Outputs
1 | 24VIN-1 | 24V DC Bus Input 1 |  |  |  | 24V+ | 24V DC | 24V DC | Red | Black | — |  | 20 AWG
2 | 24VIN-2 | 24V DC Bus Input 2 |  |  |  | 24V+ | 24V DC | 24V DC | Red | Black | — |  | 20 AWG
3 | 24VIN-3 | 24V DC Bus Input 3 |  |  |  | 24V+ | 24V DC | 24V DC | Red | Black | — |  | 20 AWG
4 | 24VIN-4 | 24V DC Bus Input 4 |  |  |  | 24V+ | 24V DC | 24V DC | Red | Black | — |  | 20 AWG
5 | 24VIN-5 | 24V DC Bus Input 5 |  |  |  | 24V+ | 24V DC | 24V DC | Red | Black | — |  | 20 AWG
1 | 24VOUT-1 | 24V DC Bus Output 1 |  |  |  | 24V+ | 24V DC | 24V DC | Red | Black | — |  | 20 AWG
2 | 24VOUT-2 | 24V DC Bus Output 2 |  |  |  | 24V+ | 24V DC | 24V DC | Red | Black | — |  | 20 AWG
3 | 24VOUT-3 | 24V DC Bus Output 3 |  |  |  | 24V+ | 24V DC | 24V DC | Red | Black | — |  | 20 AWG
4 | 24VOUT-4 | 24V DC Bus Output 4 |  |  |  | 24V+ | 24V DC | 24V DC | Red | Black | — |  | 20 AWG
5 | 24VOUT-5 | 24V DC Bus Output 5 |  |  |  | 24V+ | 24V DC | 24V DC | Red | Black | — |  | 20 AWG
0V DC BUS - POWER DISTRIBUTION ¦ 5 Inputs / 5 Outputs
1 | 0VIN-1 | 0V DC Bus Input 1 |  |  |  | 0V− | 0V DC | 0V DC | Black | — | — |  | 20 AWG
2 | 0VIN-2 | 0V DC Bus Input 2 |  |  |  | 0V− | 0V DC | 0V DC | Black | — | — |  | 20 AWG
3 | 0VIN-3 | 0V DC Bus Input 3 |  |  |  | 0V− | 0V DC | 0V DC | Black | — | — |  | 20 AWG
4 | 0VIN-4 | 0V DC Bus Input 4 |  |  |  | 0V− | 0V DC | 0V DC | Black | — | — |  | 20 AWG
5 | 0VIN-5 | 0V DC Bus Input 5 |  |  |  | 0V− | 0V DC | 0V DC | Black | — | — |  | 20 AWG
1 | 0VOUT-1 | 0V DC Bus Output 1 |  |  |  | 0V− | 0V DC | 0V DC | Black | — | — |  | 20 AWG
2 | 0VOUT-2 | 0V DC Bus Output 2 |  |  |  | 0V− | 0V DC | 0V DC | Black | — | — |  | 20 AWG
3 | 0VOUT-3 | 0V DC Bus Output 3 |  |  |  | 0V− | 0V DC | 0V DC | Black | — | — |  | 20 AWG
4 | 0VOUT-4 | 0V DC Bus Output 4 |  |  |  | 0V− | 0V DC | 0V DC | Black | — | — |  | 20 AWG
5 | 0VOUT-5 | 0V DC Bus Output 5 |  |  |  | 0V− | 0V DC | 0V DC | Black | — | — |  | 20 AWG
AC/DC CONVERTER - POWER SUPPLY ¦ 3 Inputs (L, N, PE) / 4 Outputs (++, --)
1 | ACIN-L | AC Input - Line (L) |  |  |  | L | 230V AC | 230V AC | Brown | — | — |  | AC Mains Input
2 | ACIN-N | AC Input - Neutral (N) |  |  |  | N | 230V AC | 230V AC | Blue | — | — |  | AC Mains Input
3 | ACIN-PE | AC Input - Protective Earth (PE) |  |  |  | PE | 0V / Earth | Earth | Green/Yellow | — | — |  | Earth Bonding
1 | DCOUT-1+ | DC Output 1 - Positive (+) |  |  |  | V+ | 24V DC | 24V DC | Red | — | — |  | To 24V DC Bus
2 | DCOUT-2+ | DC Output 2 - Positive (+) |  |  |  | V+ | 24V DC | 24V DC | Red | — | — |  | To 24V DC Bus
3 | DCOUT-1− | DC Output 1 - Negative (-) |  |  |  | V− | 0V DC | 0V DC | Black | — | — |  | To 0V DC Bus
4 | DCOUT-2− | DC Output 2 - Negative (-) |  |  |  | V− | 0V DC | 0V DC | Black | — | — |  | To 0V DC Bus

## Terminal Block Layout (hidden)
TERMINAL BLOCK LAYOUT - PRJ-26001
Panel ID: 1 |  | Panel Name: PCW |  | Voltage: 24 VDC / 230 V AC, 50 Hz |  |  | PLC: WAGO Compact Controller 100 (751-9402)
DIN RAIL 1 - Power Supply & Earth Terminals
TB No. | Term No. | Terminal Type | Wire Color | Cross-Section mm² | Cable No. | Cable Core | To / From | Tag / Description | Ferrule | Jumper | Notes
DIN RAIL 1 - Digital I/O Interface Terminals ¦ CC100: X12 (DI.1–8) / X5 (DIO.1–8)
TB No. | Term No. | Terminal Type | Wire Color | Cross-Section mm² | Cable No. | Cable Core | To / From | Tag / Description | Ferrule | Jumper | Notes
DIN RAIL 1 - Analog Signal Interface Terminals ¦ CC100: X13 (AI/AIO) / X14 (NI/PT)
TB No. | Term No. | Terminal Type | Wire Color | Cross-Section mm² | Cable No. | Cable Core | To / From | Tag / Description | Ferrule | Jumper | Notes

## Wiring Legend
WIRING LEGEND, COLOR CODES & STANDARDS - PRJ-26001
1. WIRE COLOR CODES — IEC 60446 / AS/NZS 3000
Function | Wire Color | Hex Code | IEC Ref | Application | Voltage Level | Ferrule Color | Notes
24V DC Positive | Red | #FF0000 | IEC 60446 | 24V DC Supply Positive | 24V DC | Red | 20 AWG / 0.5mm²
0V DC Negative | Black | #000000 | IEC 60446 | 24V DC Supply Negative / Return | 0V DC | Black | 20 AWG / 0.5mm²
Protective Earth (PE) | Green / Yellow | #00B050 / #FFFF00 | IEC 60446 | Protective Earth / Safety Grounding | 0V / Earth | Green / Yellow | 20 AWG / 0.5mm²
Line (L) - AC Live | Brown | #843C0C | IEC 60446 | L - AC Line / Live Conductor | 230V AC | Brown | 3G 1mm²
Neutral (N) - AC Neutral | Blue | #2E75B6 | IEC 60446 | N - AC Neutral Conductor | 0V AC | Blue | 3G 1mm²
Protective Earth (PE) | Green / Yellow | #00B050 / #FFFF00 | IEC 60446 | Protective Earth / Safety Grounding | 0V / Earth | Green / Yellow | 3G 1mm²
2. CABLE TYPE REFERENCE - SPECIFICATIONS
Cable Code | Cable Description | Standard | Outer Color | Temp Range | Application | Min Bend Radius | Notes
3. ABBREVIATIONS & TAG CODES
Abbreviation | Meaning | Abbreviation | Meaning
4. APPLICABLE STANDARDS & CODES
Standard | Title | Applies To | Notes
IEC 60204-1 | Safety of Machinery – Electrical Equipment | Panel wiring, control circuits, safety | Current edition
IEC 60228 | Conductors of Insulated Cables | Wire sizing and classification
IEC 60446 | Identification of Conductors by Colours | Wire colour coding | Brown/Black/Grey/Blue/G-Y
IEC 60502 | Power Cables 1kV–30kV | LV power cable specs | XLPE and PVC
IEC 60584 | Thermocouples | TC types and extension cables | J, K, T, E type
IEC 61131-2 | PLCs – Equipment Requirements | PLC hardware I/O specs | Signal levels, filtering
IEC 61156 | Data Cables for Digital Communications | Ethernet and comms cables | Cat6 and RS485
AS/NZS 3000 | Wiring Rules (Australia/NZ) | All electrical installations | Local regulatory compliance
AS/NZS 5000.1 | Electric Cables – Polymeric Insulated | LV power and control cables | Australian cable standard
IEC 61000-4-5 | EMC – Surge Immunity | Panel surge protection | Cable segregation distances
5. WAGO CC100 (751-9402) I/O CONNECTOR REFERENCE
Connector | Channel(s) | Signal Type | CODESYS Address
X11 | DI.1 – DI.8 (8 channels) | Digital Input 24VDC, sinking, 2.8 mA | %IX0.0 – %IX0.7
X12 | DIO.1 – DIO.8 (8 channels) | Configurable DI or DO 24VDC, 0.5 A | %IX1.0–%IX1.7 / %QX1.0–%QX1.7
X13 (AI) | AI.1 – AI.2 (2 channels) | Analog Input 4-20 mA / 0-10 V, 16-bit | %IW0, %IW2
X13 (AIO) | AIO.1 – AIO.2 (2 channels) | Configurable AI or AO 4-20 mA / 0-10 V | %IW4, %IW6 / %QW0, %QW2
X14 (NI/PT) | NI.1 – NI.2 (2 channels) | NI1000 / PT1000 RTD temperature input | %IW8, %IW10
RS-485 (×2) | Port 1 and Port 2 | RS-485 serial: Modbus RTU, custom serial | SysLibCom / ModbusRTU lib
Ethernet (×2) | X1 (ETH1), X2 (ETH2) | Modbus TCP, PROFINET, EtherCAT, BACnet, MQTT | Configured via WBM / CODESYS

## Cable Drum Register (hidden)
CABLE DRUM REGISTER - PRJ-26001
Project: PRJ-26001 ¦ Site: Building J - Cyber3Lab, Howest Brugge, Belgium ¦ Maintained By: Electrical Foreman
# | Drum ID | Cable Type & Spec | Core Qty | Core Size | Volt Rating | Full Length (m) | Issued (m) | Remaining (m) | Location / Bay | Date Received | Supplier | Remarks
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25